TECHNICAL EVALUATION REPORT

To: GM/Supply Chain Management

Through: Relevant User Department CXO

| Subject: Supply, installation and commissioning of 60kVA UPS systems for Regional Data Centres |  |
| --- | --- |
| Tender No: SCMD/TET/2026/014 | User Department: Network Operations |
| Forwarded by: Mr. K. Silva, CXO - Network |  |
| Budget Confirmed: 1. CAPEX: LKR 48,000,000 2. OPEX: - | Previous JTB Reference (if any) JTB Ref No: - Date: - |

3. Background:
Relevant approval: Governance Board approval GB/2026/18 dated 12-06-2026.
Method of tendering: Open Tender
Procurement process up to bid opening: Tender floated 03-08-2026; bidders' conference 10-08-2026; one 5-day extension; closed 24-08-2026; opened 25-08-2026.

Tender Timeline

| Tender Published Date | 03-08-2026 |
| --- | --- |
| Tender Closed Date | 24-08-2026 |
| Technical Bid Opened Date | 25-08-2026 |
| TET Report Submission Date | 10-09-2026 |
| Bid Bond Expiry Date (s) | 24-11-2026 (ABC); 30-11-2026 (XYZ); 27-11-2026 (Delta) |

| i. | Purpose of the tender: Selection of suppliers for UPS units for the Regional Data Centre upgrade project during 2026/27. |
| --- | --- |
| ii. iii. | Short description of goods/services: Supply, installation, commissioning and training for 4 x 60kVA UPS units with 36-month warranty. Delivery within 12 weeks. |
| iv. | etc ... |

4. Observations:
Compliance with General Conditions: Compliant
Compliance with Contract Conditions: Compliant
Bidder 1: ABC Power (Pvt) Ltd
Compliance with Technical Conditions: Compliant
Compliance with Special Conditions: Compliant
Minor/Acceptable Non-compliances: 3-year warranty quoted instead of 5-year
Bidder 2: XYZ Energy Solutions
Compliance with Technical Conditions: Non-compliant
Compliance with Special Conditions: Compliant
Major Non-compliances (disqualifying): No letter of authority; battery autonomy 8 min vs 15 min required
Impact of Non-compliances: Cannot meet the critical backup requirement
Qualified / Disqualified: Disqualified
Delta Power Ltd
Compliance with Technical Conditions: Compliant
Compliance with Special Conditions: Compliant
Commercial terms to be negotiated:
ABC Power (Pvt) Ltd - payment terms to be revised to 30/60/10
Delta Power Ltd - LD clause to be negotiated

5. Recommendations:
Recommended for Financial Bid Opening:
ABC Power (Pvt) Ltd - Yes
XYZ Energy Solutions - No
Delta Power Ltd - Yes
Evaluated BOM included? Yes
Previous purchase price: 2024 - 3 units of 60kVA UPS at LKR 3.1M each
More Suitable:
ABC Power (Pvt) Ltd - 1st place
Delta Power Ltd - 2nd place

| i. | How the need arose: Existing UPS units reached end of life; replacement required under the DC upgrade project. |
| --- | --- |
| ii. |  |
| iii. | For renewal of service contract indicated existing contract period and reasons to extend etc. … etc….. |
| iv. |  |

| i. | Project No. and name: PRJ-2026-044 Regional DC Upgrade Account Code and Cost Center: N/A (CAPEX) Budget reserved out of total available: LKR 48M of LKR 120M |
| --- | --- |
| ii. |  |

| Bidder‟s Name | Local Agent | Letter of Authority | Product Brand and Model | Bid Validity as mentioned in bid | Expiry date of bid bond |
| --- | --- | --- | --- | --- | --- |
| 1 ABC Power (Pvt) Ltd | Yes - Mr. Fernando | Yes | Eaton 93PM 60kVA | 120 days | 24-11-2026 |
| XYZ Energy Solutions | No | No | Schneider Galaxy VS 60kVA | 90 days | 30-11-2026 |
| Delta Power Ltd | Yes - Ms. Perera | Yes | Vertiv Liebert APM 60kVA | 120 days | 27-11-2026 |

| i. | Each recommended bid shall carry evaluated BOM for pricing exactly in line with the prices quoted by the bidder1 (soft copy is required in Excel format). If training, Pre-shipment Inspection, spare parts, services (installation, testing, commissioning etc) are needed to be indicated with quantities. If AMC is not included in the tender, clear statement to the effect that ‘AMC is not required for this project/Procurement’ to be given. Warranty period included. |
| --- | --- |
| ii. |  |
| iii. |  |
| iv. | Any other items that should be accounted for commercial evaluation with relevant guidance. |

6. Self-Declaration by the Members of the Evaluation Team:

I confirm that to the best of my knowledge I do not have any direct or indirect interest / relationship with any of the suppliers who have quoted for the tender under review. I am being a member of the TET/CET for this procurement confirm that I am aware that it is a punishable offence under the Company policies, rules and regulation and also under the other statutes as applicable that non - disclosure of my conflict of interest on any of the tenders or procurements.

In the event of me becoming aware of any changes to my declaration, I shall notify the GM–Supply Chain Management in writing within 3 days of becoming aware of any conflict of interest indicating the Tender number and refrain from participating in the tender evaluation.

# 7. Submitted by:

|  | Name | Designation | Relevance to TET | Signature |
| --- | --- | --- | --- | --- |
| 1 | Mr. R. Jayasinghe | DGM Network | Chairman/TET |  |
| 2 | Ms. S. Dias | Manager IT | Member/TET |  |
| 3 |  |  | Member/TET |  |
| 4 |  |  | Member/TET |  |